Sprinkler Inspection Certificate
For
	TAMPA SPORTS AUTHORITY		
	4201 N. DALE MABRY HWY		
	TAMPA, FL 33607		
Tested to NFPA 25 Standards
This Inspection was performed in accordance with applicable NFPA Standards.  The subsequent pages of this report provide performance measurements, listed ranges of acceptable results, and complete documentation of the inspection.  Whenever discrepancies exist between acceptable performance standards and actual test results, notes and/or recommended solutions have been proposed or provided for immediate review and approval.

Inspection Date
Dec 22, 2020
Building: TAMPA SPORTS AUTHORITY	Company: Fire & Life Safety America, Inc. - Tampa	
Contact: Deltecia Jones	Contact: Tyson L. Mendel	
Title: Procurement Manager	Title: Inspector	

Executive Summary
Generated by: BuildingReports.com

Building Information	
  Building: TAMPA SPORTS AUTHORITY	Contact: Deltecia Jones	
  Address: 4201 N. DALE MABRY HWY	Phone: 8133506511	
  Address: 	Fax: 	
  City/State/Zip: TAMPA, FL 33607	Mobile: 	
  Country: United States of America	Email: djones@tampasportsauthority.com	
Inspection Performed By	
  Company: Fire & Life Safety America, Inc. - Tampa	Inspector: Tyson L. Mendel	
  Address: 5915 Causeway Blvd	Phone: 813-513-9331	
  Address: 	Fax: 	
  City/State/Zip: Tampa, FL 33619	Mobile: 813-440-8475	
  Country: United States of America	Email: tlmendel@flsamerica.com	
System Control Unit	
System Type	System Location	Protected Area	Devices	
  Fire Pump	  	  	  29	
  Preaction	  	  Control Room	  15	
  Service Main	  	  	  9	
  Standpipe	  	  Quad A	  17	
  Standpipe	  	  Quad B	  19	
  Standpipe	  	  Quad C	  16	
  Standpipe	  	  Quad D	  24	
  Standpipe	  	  Stairway #6	  22	
  Standpipe	  	  Stairway #7	  27	
  Wet Pipe	  	  	  2	
  Wet Pipe	  	  Pirate Ship	  12	
  Wet Pipe	  	  Quad A	  38	
  Wet Pipe	  	  Quad B	  14	
  Wet Pipe	  	  Quad C	  28	
  Wet Pipe	  	  Quad D	  7	
  Wet Pipe	  	  field	  1	
  Wet Pipe	  	  sideline	  1	

Inspection Summary	
Category	Total Items	Serviced	Passed	Failed/Other	
	Qty	%	Qty	%	Qty	%	Qty	%	
  Device	39	13.88%	39	100.00%	39	100.00%	0	0%	
  Alarm	80	28.47%	77	96.25%	77	100.00%	0	0%	
  Valve	75	26.69%	70	93.33%	70	100.00%	0	0%	
  Hose	69	24.56%	60	86.96%	58	96.67%	2	3.33%	
  Pump	9	3.20%	9	100.00%	9	100.00%	0	0%	
  Sprinkler	9	3.20%	5	55.56%	5	100.00%	0	0%	
Totals	281	100%	260	92.53%	258	99.23%	2	0.77%	
Certification	
Company: Fire & Life Safety America, Inc. - Tampa	  Building: TAMPA SPORTS AUTHORITY	
Inspector: Tyson L. Mendel	  Contact: Deltecia Jones	
		
  Signed: Dec 22, 2020 6:45:43 PM	  Signed: Dec 22, 2020 1:10:22 PM	

Discrepancy Report
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY	
The Discrepancy Report consolidates each discrepancy listed within the various Testing sections of your Inspection. Discrepancies are listed by Category, and grouped by device type. The description of the problem is provided and where appropriate, code references are listed for your convenience. Any item that was inspected that is subject to a recall or part of a manufacturer’s replacement/upgrade program is included.	
Device Type	 Manufacturer	 ModelNumber	 Date	Qty	
Items listed for Recall or Replacement/Upgrade	
No items found during this inspection.	

& ScanID	` Location	L Problem	& Reference	
Standpipe, Quad A	
Critical Deficiencies	
Fire Dep't Connection	
49546380	Quad A FDC	Rusted/Corroded	NFPA25 13.7.1 (2) (3)	
Standpipe, Stairway #7	
Hose Connection	
49546410	1st Stairway #7	Leaking	NFPA25 4.1.5.1	
Code References	
NFPA25 13.7.1 (2) (3)	Fire department connections shall be inspected quarterly to verify the following: Couplings or swivels are not damaged and rotate smoothly. Plugs or caps are in place and undamaged.	
NFPA25 4.1.5.1	The property owner or designated representative shall correct or repair deficiencies or impairments that are found during the inspection, test, and maintenance required by this standard.	

Proposed Solutions Report	
Generated by: BuildingReports.com	
Building: TAMPA SPORTS AUTHORITY	
The Proposed Solution Report provides a solution for each discrepancy listed on the Discrepancy Report.  Provide a check mark where indicated to approve repairs listed within the report. Items listed as T/M are available for repair on a Time and Materials basis.	

ScanID	Location	Solution	Model #	Cost	Fix	
Standpipe, Quad A	
Critical Deficiencies	
Fire Dep't Connection	
49546380	Quad A FDC	Replace	unknown	T/M	¨	
Standpipe, Stairway #7	
Hose Connection	
49546410	1st Stairway #7	Correct	unknown	T/M	¨	
PO #: (none)	T/M		

Inspection & Testing
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY	
The Inspection & Testing section lists all of the items inspected in your building.  Items are grouped by Passed or Failed/Other. Items are listed by Category. Each item includes the services performed, and the time & date at which testing occurred.	

Device Type	Location	Service	Time	Date	
Passed	
Fire Pump	
Tamper Switch	Fire Pump Suction	Quarterly	7:42:23 AM	12/22/2020	
Tamper Switch	Fire Pump Test Header	Quarterly	7:48:05 AM	12/22/2020	
Tamper Switch	Fire Pump Discharge	Quarterly	7:48:50 AM	12/22/2020	
Tamper Switch	Fire Pump Bypass	Quarterly	7:50:36 AM	12/22/2020	
Tamper Switch	Fire Pump Bypass	Quarterly	7:51:15 AM	12/22/2020	
Gauge	Fire Pump Controller	Quarterly	7:42:29 AM	12/22/2020	
Gauge	Fire Pump Relief Valve	Quarterly	7:45:40 AM	12/22/2020	
Gauge	Fire Pump Relief Valve	Quarterly	7:46:03 AM	12/22/2020	
Gauge	Jockey Pump Discharge	Quarterly	7:49:03 AM	12/22/2020	
Gauge	Jockey Pump Controller	Quarterly	7:49:32 AM	12/22/2020	
Gauge	Jockey Pump Suction	Quarterly	7:49:44 AM	12/22/2020	
Gauge	Jockey Pump Controller	Quarterly	7:51:54 AM	12/22/2020	
Controller	Pump Room	Quarterly	7:43:18 AM	12/22/2020	
Electrical Driver	Fire Pump Room	Quarterly	7:43:54 AM	12/22/2020	
Fire Pump Gauge	Jockey Pump Discharge	Quarterly	7:44:20 AM	12/22/2020	
Fire Pump Gauge	Jockey Pump Discharge	Quarterly	7:45:36 AM	12/22/2020	
Jockey Controller	Jockey Pump Controller	Quarterly	7:51:48 AM	12/22/2020	
Jockey Pump	Fire Pump Room	Quarterly	7:49:38 AM	12/22/2020	
Pump	Fire Pump Room	Quarterly	6:49:18 PM	12/22/2020	
Signage	Control Room	Quarterly	12:56:32 PM	12/22/2020	
Signage	Home Team Locker Room	Quarterly	12:56:33 PM	12/22/2020	
Signage	Team Store Atrium	Quarterly	12:56:35 PM	12/22/2020	
Control Valve	Fire Pump Suction	Quarterly	7:42:22 AM	12/22/2020	
Control Valve	Fire Pump Test Header	Quarterly	7:47:52 AM	12/22/2020	
Control Valve	Jockey Pump Discharge	Quarterly	7:48:43 AM	12/22/2020	
Control Valve	Fire Pump Discharge	Quarterly	7:49:02 AM	12/22/2020	
Control Valve	Jockey Pump Suction	Quarterly	7:50:13 AM	12/22/2020	
Control Valve	Fire Pump Bypass	Quarterly	7:50:29 AM	12/22/2020	
Control Valve	Fire Pump Bypass	Quarterly	7:51:28 AM	12/22/2020	
Preaction, Control Room	
Control Panel	Upper Suite A Control Room	Quarterly	12:06:06 PM	12/22/2020	
Pressure Switch	Upper Suite A Control Room Pressure Switch	Quarterly	12:11:18 PM	12/22/2020	
Pressure Switch	Control Room Alarm Air Pressure	Quarterly	12:14:01 PM	12/22/2020	
Tamper Switch	Control Room Low Air	Quarterly	12:08:25 PM	12/22/2020	
Drain	Control Room	Quarterly	12:14:59 PM	12/22/2020	
Gauge	Control Room	Quarterly	12:09:34 PM	12/22/2020	
Gauge	Control Room	Quarterly	12:09:59 PM	12/22/2020	
Gauge	Control Room	Quarterly	12:10:15 PM	12/22/2020	
Gauge	Control Room	Quarterly	12:10:33 PM	12/22/2020	
Gauge	Control Room	Quarterly	12:10:58 PM	12/22/2020	
Gauge	Control Room	Quarterly	12:13:19 PM	12/22/2020	
Air Compressor	Control Room Low Air	Quarterly	12:14:34 PM	12/22/2020	
Air Maintenance Device	Control Room	Quarterly	12:13:33 PM	12/22/2020	
Control Valve	Upper Suite A Control Room Main Control	Quarterly	12:07:49 PM	12/22/2020	
Preaction Valve	Control Room	Quarterly	12:08:42 PM	12/22/2020	
Standpipe, Quad A	
Tamper Switch	Quad A Housekeeping / Field Entry M1-9	Quarterly	8:02:19 AM	12/22/2020	
Tamper Switch	Quad A Housekeeping / Ramp M1-50	Quarterly	8:03:32 AM	12/22/2020	
Tamper Switch	Quad A Mechanical Room M1-22	Quarterly	8:04:49 AM	12/22/2020	
Hose Connection	2nd Quad A Main Concourse	Quarterly	9:45:59 AM	12/22/2020	
Hose Connection	4th Quad A Club Level	Quarterly	11:51:13 AM	12/22/2020	
Hose Connection	5th Quad A Lower Suite	Quarterly	11:57:58 AM	12/22/2020	
Hose Connection	6th Quad A Upper Suite	Quarterly	12:04:27 PM	12/22/2020	
Hose Connection	7th Quad A Upper Concourse	Quarterly	10:07:08 AM	12/22/2020	
Hose Connection	Quad A Catering Warehouse	Quarterly	7:59:26 AM	12/22/2020	
Hose Connection	Quad A Ramp	Quarterly	8:03:05 AM	12/22/2020	
Hose Connection	Quad A Mechanical Room	Quarterly	8:04:45 AM	12/22/2020	
Hose Connection	Quad A Players Corridor	Quarterly	8:10:17 AM	12/22/2020	
Hose Connection	Quad A Field Entry	Quarterly	8:49:58 AM	12/22/2020	
Control Valve	Quad A Housekeeping / Field Entry M1-9	Quarterly	8:02:27 AM	12/22/2020	
Control Valve	Quad A Housekeeping / Ramp M1-50	Quarterly	8:03:47 AM	12/22/2020	
Control Valve	Quad A Mechanical Room M1-22	Quarterly	8:05:00 AM	12/22/2020	
Standpipe, Quad B	
Tamper Switch	Quad B Delivery Swing Gate M1-49	Quarterly	8:53:51 AM	12/22/2020	
Tamper Switch	Quad B Chiller M1-47	Quarterly	8:55:21 AM	12/22/2020	
Fire Dep't Connection	Quad B FDC	Quarterly	7:22:31 AM	12/22/2020	
Hose Connection	2nd Quad B Main Concourse	Quarterly	9:32:59 AM	12/22/2020	
Hose Connection	4th Quad B / C Club Level	Quarterly	11:27:51 AM	12/22/2020	
Hose Connection	4th Quad B Club Level	Quarterly	12:30:04 PM	12/22/2020	
Hose Connection	5th Quad B / C Lower Suite	Quarterly	11:30:12 AM	12/22/2020	
Hose Connection	5th Quad B Lower Suite	Quarterly	12:32:00 PM	12/22/2020	
Hose Connection	6th Quad B / C Ford Super Suite	Quarterly	11:32:46 AM	12/22/2020	
Hose Connection	6th Quad B Ford Super Suite Pantry / Stairway 2	Quarterly	12:39:05 PM	12/22/2020	
Hose Connection	7th Quad B Upper Concourse	Quarterly	10:53:43 AM	12/22/2020	
Hose Connection	Quad B Delivery Swing Gate	Quarterly	7:53:34 AM	12/22/2020	
Hose Connection	Quad B Field Entry	Quarterly	8:39:46 AM	12/22/2020	
Hose Connection	Quad B East Club/Suite Lobby Hall	Quarterly	8:40:48 AM	12/22/2020	
Hose Connection	Quad B Chiller	Quarterly	8:55:10 AM	12/22/2020	
Control Valve	Quad B Delivery Swing Gate M1-49	Quarterly	7:52:56 AM	12/22/2020	
Control Valve	Quad B Chiller M1-47	Quarterly	8:55:35 AM	12/22/2020	
Standpipe, Quad C	
Tamper Switch	Quad C Tunnel / Grounds Crew M1-26	Quarterly	8:34:09 AM	12/22/2020	
Tamper Switch	Quad C Middle Hall M1-24	Quarterly	8:42:12 AM	12/22/2020	
Tamper Switch	Quad C Mechanical M1-34	Quarterly	11:13:23 AM	12/22/2020	
Fire Dep't Connection	Quad C FDC	Quarterly	9:12:19 AM	12/22/2020	
Hose Connection	2nd Quad C Main Concourse	Quarterly	9:35:03 AM	12/22/2020	
Hose Connection	4th Quad C Club Level	Quarterly	12:48:46 PM	12/22/2020	
Hose Connection	5th Quad C Lower Suite	Quarterly	12:48:06 PM	12/22/2020	
Hose Connection	6th Quad C Upper Suite	Quarterly	12:44:43 PM	12/22/2020	
Hose Connection	7th Quad C Upper Concourse	Quarterly	10:55:06 AM	12/22/2020	
Hose Connection	Quad C Tunnel / Grounds Crew	Quarterly	8:34:41 AM	12/22/2020	
Hose Connection	Quad C Mechanical	Quarterly	8:35:58 AM	12/22/2020	
Hose Connection	Quad C Field Entry	Quarterly	8:38:16 AM	12/22/2020	
Hose Connection	Quad C Middle Hall	Quarterly	8:41:23 AM	12/22/2020	
Control Valve	Quad C Tunnel / Grounds Crew M1-26	Quarterly	8:34:18 AM	12/22/2020	
Control Valve	Quad C Middle Hall M1-24	Quarterly	8:42:08 AM	12/22/2020	
Control Valve	Quad C Mechanical M1-34	Quarterly	9:17:27 AM	12/22/2020	
Standpipe, Quad D	
Tamper Switch	Quad D Players Entrance M1-25	Quarterly	8:11:43 AM	12/22/2020	
Tamper Switch	Quad D Roll Up Door M1-27	Quarterly	8:26:12 AM	12/22/2020	
Tamper Switch	Quad D Mechanical M1-30	Quarterly	8:27:04 AM	12/22/2020	
Tamper Switch	Quad D TSA Hall M1-29	Quarterly	8:32:56 AM	12/22/2020	
Tamper Switch	Quad D Buccs Warehouse HR Door 2 locker	Quarterly	11:16:21 AM	12/22/2020	
Fire Dep't Connection	Quad D FDC	Quarterly	9:08:41 AM	12/22/2020	
Hose Connection	2nd Quad D Main Concourse	Quarterly	9:44:43 AM	12/22/2020	
Hose Connection	4th Quad A / D Club Level	Quarterly	11:53:22 AM	12/22/2020	
Hose Connection	4th Quad D Club Level	Quarterly	11:54:23 AM	12/22/2020	
Hose Connection	5th Quad A / D Lower Suite	Quarterly	11:59:34 AM	12/22/2020	
Hose Connection	5th Quad D Lower Suite	Quarterly	12:00:29 PM	12/22/2020	
Hose Connection	6th Quad D	Quarterly	10:14:47 AM	12/22/2020	
Hose Connection	6th Quad A / D Press Box	Quarterly	12:18:06 PM	12/22/2020	
Hose Connection	6th Quad D Press Box	Quarterly	12:21:15 PM	12/22/2020	
Hose Connection	Quad D Players Corridor	Quarterly	8:10:47 AM	12/22/2020	
Hose Connection	Quad D Roll Up Door	Quarterly	8:23:57 AM	12/22/2020	
Hose Connection	Quad D TSA Hall	Quarterly	8:32:29 AM	12/22/2020	
Hose Connection	Quad D Field Entry	Quarterly	8:48:16 AM	12/22/2020	
Hose Connection	Quad D Mechanical	Quarterly	9:18:30 AM	12/22/2020	
Control Valve	Quad D Players Entrance M1-25	Quarterly	8:11:36 AM	12/22/2020	
Control Valve	Quad D Roll Up Door M1-27	Quarterly	8:26:22 AM	12/22/2020	
Control Valve	Quad D Mechanical M1-30	Quarterly	8:27:15 AM	12/22/2020	
Control Valve	Quad D TSA Hall M1-29	Quarterly	8:33:06 AM	12/22/2020	
Control Valve	Quad D Buccs Warehouse HR Door 2 locker	Quarterly	11:16:10 AM	12/22/2020	
Standpipe, Stairway #6	
Tamper Switch	2nd Stairway #6 M2-15	Quarterly	11:08:45 AM	12/22/2020	
Tamper Switch	3rd Stairway #6 M2-14	Quarterly	11:08:05 AM	12/22/2020	
Tamper Switch	4th Stairway #7 M2-13 Club Level	Quarterly	11:07:24 AM	12/22/2020	
Tamper Switch	5th Stairway #6 M2-24 Lower Suite	Quarterly	11:06:36 AM	12/22/2020	
Tamper Switch	6th Stairway #6 M2-35 Upper Suite	Quarterly	11:05:35 AM	12/22/2020	
Waterflow Switch	4th Stairway #6 Club Level	Quarterly	11:07:21 AM	12/22/2020	
Waterflow Switch	5th Stairway #6 Lower Suite	Quarterly	11:06:30 AM	12/22/2020	
Waterflow Switch	6th Stairway #6 Upper Suite	Quarterly	11:05:25 AM	12/22/2020	
Gauge	7th Stairway #6	Quarterly	11:04:33 AM	12/22/2020	
Hose Connection	1st Stairway #6	Quarterly	11:10:54 AM	12/22/2020	
Hose Connection	3rd Stairway #6	Quarterly	11:07:59 AM	12/22/2020	
Hose Connection	4th Stairway #6	Quarterly	11:07:35 AM	12/22/2020	
Hose Connection	5th Stairway #6	Quarterly	11:06:45 AM	12/22/2020	
Hose Connection	7th Stairway #6	Quarterly	11:04:30 AM	12/22/2020	
Control Valve	2nd Stairway #6 M2-15	Quarterly	11:08:53 AM	12/22/2020	
Control Valve	3rd Stairway #6 M2-14	Quarterly	11:08:20 AM	12/22/2020	
Control Valve	4th Stairway #7 M2-13 Club Level	Quarterly	11:07:31 AM	12/22/2020	
Control Valve	5th Stairway #6 M2-24 Lower Suite	Quarterly	11:06:43 AM	12/22/2020	
Control Valve	6th Stairway #6 M2-35 Upper Suite	Quarterly	11:05:46 AM	12/22/2020	
Inspector's Test	4th Stairway #6 Club Level	Quarterly	11:07:04 AM	12/22/2020	
Inspector's Test	5th Stairway #6 Lower Suite	Quarterly	11:06:23 AM	12/22/2020	
Inspector's Test	6th Stairway #6 Upper Suite	Quarterly	11:05:10 AM	12/22/2020	
Standpipe, Stairway #7	
Tamper Switch	2nd Stairway #7 M2-5	Quarterly	10:28:45 AM	12/22/2020	
Tamper Switch	3rd Stairway #7 M2-29	Quarterly	10:28:05 AM	12/22/2020	
Tamper Switch	4th Stairway #7 M2-7 Club Level	Quarterly	10:25:36 AM	12/22/2020	
Tamper Switch	5th Stairway #7 M2-7 Lower Suite	Quarterly	10:23:46 AM	12/22/2020	
Tamper Switch	6th Stairway #7 M2-57 Upper Suite	Quarterly	10:24:19 AM	12/22/2020	
Waterflow Switch	4th Stairway #7 M2-99 Club Level	Quarterly	10:24:59 AM	12/22/2020	
Waterflow Switch	5th Stairway #7 Lower Suite	Quarterly	10:23:16 AM	12/22/2020	
Waterflow Switch	6th Stairway #7 Upper Suite	Quarterly	10:21:14 AM	12/22/2020	
Gauge	4th Stairway #7 M2-99 Atrium	Quarterly	10:25:57 AM	12/22/2020	
Gauge	7th Stairway #7	Quarterly	10:20:24 AM	12/22/2020	
Hose Connection	5th Stairway #7	Quarterly	10:23:04 AM	12/22/2020	
Hose Connection	6th Stairway #7	Quarterly	10:21:08 AM	12/22/2020	
Hose Connection	7th Stairway #7	Quarterly	10:20:09 AM	12/22/2020	
Hose Connection	7th Stairway #7	Quarterly	10:20:18 AM	12/22/2020	
Control Valve	2nd Stairway #7 M2-5	Quarterly	10:28:41 AM	12/22/2020	
Control Valve	3rd Stairway #7 M2-29	Quarterly	10:27:57 AM	12/22/2020	
Control Valve	4th Stairway #7 M2-7 Club Level	Quarterly	10:25:47 AM	12/22/2020	
Control Valve	4th Stairway #7 M2-99 Atrium	Quarterly	10:26:29 AM	12/22/2020	
Control Valve	5th Stairway #7 M2-7 Lower Suite	Quarterly	10:23:59 AM	12/22/2020	
Control Valve	6th Stairway #7 M2-57 Upper Suite	Quarterly	10:24:22 AM	12/22/2020	
Inspector's Test	4th Stairway #7 Club Level	Quarterly	10:25:03 AM	12/22/2020	
Inspector's Test	5th Stairway #7 Lower Suite	Quarterly	10:23:30 AM	12/22/2020	
Inspector's Test	6th Stairway #7 Upper Suite	Quarterly	10:21:27 AM	12/22/2020	
Wet Pipe, field	
Hose Connection	East sideline on field	Quarterly	8:38:45 AM	12/22/2020	
Wet Pipe, Pirate Ship	
Tamper Switch	Under Ship M-46	Quarterly	9:21:34 AM	12/22/2020	
Waterflow Switch	Under Ship	Quarterly	9:23:36 AM	12/22/2020	
Drain	Under Ship	Quarterly	9:23:56 AM	12/22/2020	
Gauge	Under Ship	Quarterly	9:22:06 AM	12/22/2020	
Gauge	Under Ship	Quarterly	9:22:46 AM	12/22/2020	
Alarm Valve	Under Ship	Quarterly	9:21:13 AM	12/22/2020	
Control Valve	Under Ship M-46	Quarterly	9:21:31 AM	12/22/2020	
Inspector's Test	Under Ship	Quarterly	9:23:40 AM	12/22/2020	
Wet Pipe, Quad A	
Tamper Switch	2nd Quad A Main Concourse M1-51	Quarterly	9:47:13 AM	12/22/2020	
Tamper Switch	2nd Quad A Main Concourse M1-41	Quarterly	9:49:51 AM	12/22/2020	
Tamper Switch	7th Quad A Upper Concourse M2-75	Quarterly	10:10:00 AM	12/22/2020	
Tamper Switch	Quad A Catering Warehouse Restroom / Kitchen M1-	Quarterly	8:01:20 AM	12/22/2020	
Tamper Switch	Quad A Undeveloped Space M1-21	Quarterly	8:08:14 AM	12/22/2020	
Tamper Switch	Quad A Undeveloped Space	Quarterly	8:08:20 AM	12/22/2020	
Tamper Switch	Quad A Owners Parking M1-16	Quarterly	8:16:29 AM	12/22/2020	
Tamper Switch	Quad A Catering Warehouse M1-76	Quarterly	8:51:57 AM	12/22/2020	
Waterflow Switch	2nd Quad A Main Concourse	Quarterly	9:49:44 AM	12/22/2020	
Waterflow Switch	7th Quad A Upper Concourse	Quarterly	10:10:09 AM	12/22/2020	
Waterflow Switch	Quad A Undeveloped Space	Quarterly	8:08:25 AM	12/22/2020	
Waterflow Switch	Quad A Undeveloped Space	Quarterly	8:08:32 AM	12/22/2020	
Waterflow Switch	Quad A Owners Parking	Quarterly	8:16:13 AM	12/22/2020	
Drain	2nd Quad A Main Concourse M1-41	Quarterly	9:47:42 AM	12/22/2020	
Drain	2nd Quad A Main Concourse M1-41	Quarterly	9:50:09 AM	12/22/2020	
Drain	7th Quad A Upper Concourse	Quarterly	10:09:24 AM	12/22/2020	
Gauge	2nd Quad A Main Concourse	Quarterly	9:48:03 AM	12/22/2020	
Gauge	2nd Quad A Main Concourse	Quarterly	9:48:24 AM	12/22/2020	
Gauge	2nd Quad A Main Concourse	Quarterly	9:50:40 AM	12/22/2020	
Gauge	2nd Quad A Main Concourse	Quarterly	9:51:06 AM	12/22/2020	
Gauge	7th Quad A Upper Concourse	Quarterly	10:08:28 AM	12/22/2020	
Gauge	7th Quad A Upper Concourse	Quarterly	10:08:54 AM	12/22/2020	
Gauge	Quad A Owners Parking	Quarterly	8:15:35 AM	12/22/2020	
Signage	Quad A Owners Parking RJ Corridor	Quarterly	8:16:38 AM	12/22/2020	
Signage	Quad A Owners Parking RJ Parking	Quarterly	8:16:52 AM	12/22/2020	
Alarm Valve	2nd Quad A Main Concourse	Quarterly	9:47:35 AM	12/22/2020	
Alarm Valve	2nd Quad A Main Concourse	Quarterly	9:50:30 AM	12/22/2020	
Alarm Valve	7th Quad A Upper Concourse	Quarterly	10:08:24 AM	12/22/2020	
Control Valve	2nd Quad A Main Concourse M1-51	Quarterly	9:47:10 AM	12/22/2020	
Control Valve	2nd Quad A Main Concourse M1-41	Quarterly	9:50:01 AM	12/22/2020	
Control Valve	7th Quad A Upper Concourse M2-75	Quarterly	10:09:57 AM	12/22/2020	
Control Valve	Quad A Catering Warehouse Restroom / Kitchen M1-	Quarterly	8:01:32 AM	12/22/2020	
Control Valve	Quad A Undeveloped Space M1-21	Quarterly	8:08:42 AM	12/22/2020	
Control Valve	Quad A Undeveloped Space M1-19	Quarterly	8:08:50 AM	12/22/2020	
Control Valve	Quad A Owners Parking M1-16	Quarterly	8:16:26 AM	12/22/2020	
Control Valve	Quad A Catering Warehouse M1-76	Quarterly	8:52:10 AM	12/22/2020	
Inspector's Test	Quad A Owners Parking	Quarterly	8:18:37 AM	12/22/2020	
Wet Pipe, Quad B	
Tamper Switch	Quad B Engineering M1-33	Quarterly	7:40:37 AM	12/22/2020	
Tamper Switch	Quad B Boiler M1-38	Quarterly	7:55:06 AM	12/22/2020	
Tamper Switch	Quad B Boiler M1-39	Quarterly	7:55:21 AM	12/22/2020	
Tamper Switch	Quad B Food Vending M1-40	Quarterly	7:56:37 AM	12/22/2020	
Tamper Switch	Quad B Food Vending M1-37	Quarterly	7:56:43 AM	12/22/2020	
Tamper Switch	Quad B East Club/Suite Lobby Hall M1-35	Quarterly	8:58:24 AM	12/22/2020	
Waterflow Switch	Quad B East Club/Suite Lobby Hall	Quarterly	8:58:43 AM	12/22/2020	
Waterflow Switch	Quad B East Club/Suite Lobby Hall	Quarterly	8:58:47 AM	12/22/2020	
Control Valve	Quad B Engineering M1-33	Quarterly	7:41:09 AM	12/22/2020	
Control Valve	Quad B Boiler M1-38	Quarterly	7:55:18 AM	12/22/2020	
Control Valve	Quad B Boiler M1-39	Quarterly	7:55:33 AM	12/22/2020	
Control Valve	Quad B Food Vending M1-37	Quarterly	7:57:00 AM	12/22/2020	
Control Valve	Quad B Food Vending M1-40	Quarterly	7:57:08 AM	12/22/2020	
Control Valve	Quad B East Club/Suite Lobby Hall M1-35	Quarterly	8:58:40 AM	12/22/2020	
Wet Pipe, Quad C	
Tamper Switch	2nd Quad C Main Concourse M1-45	Quarterly	9:35:56 AM	12/22/2020	
Tamper Switch	2nd Quad C Main Concourse M1-45	Quarterly	9:38:17 AM	12/22/2020	
Tamper Switch	7th Quad C Upper Concourse M2-46	Quarterly	10:56:08 AM	12/22/2020	
Tamper Switch	Quad C Grounds Crew Storage Cage M1-29	Quarterly	8:44:49 AM	12/22/2020	
Tamper Switch	Quad C Grounds Crew Storage Cage M1-30	Quarterly	8:45:08 AM	12/22/2020	
Waterflow Switch	2nd Quad C Main Concourse M-46	Quarterly	9:36:13 AM	12/22/2020	
Waterflow Switch	2nd Quad C Main Concourse M-50	Quarterly	9:39:08 AM	12/22/2020	
Waterflow Switch	7th Quad C Upper Concourse	Quarterly	10:57:10 AM	12/22/2020	
Waterflow Switch	Quad C Grounds Crew Storage Cage	Quarterly	8:44:53 AM	12/22/2020	
Waterflow Switch	Quad C Grounds Crew Storage Cage	Quarterly	8:45:11 AM	12/22/2020	
Drain	2nd Quad C Main Concourse	Quarterly	9:39:26 AM	12/22/2020	
Drain	2nd Quad C Main Concourse	Quarterly	9:39:41 AM	12/22/2020	
Drain	7th Quad C Upper Concourse	Quarterly	11:18:44 AM	12/22/2020	
Gauge	2nd Quad C Main Concourse	Quarterly	9:36:33 AM	12/22/2020	
Gauge	2nd Quad C Main Concourse	Quarterly	9:37:36 AM	12/22/2020	
Gauge	2nd Quad C Main Concourse	Quarterly	9:38:28 AM	12/22/2020	
Gauge	2nd Quad C Main Concourse	Quarterly	9:38:45 AM	12/22/2020	
Gauge	7th Quad C Upper Concourse	Quarterly	10:56:32 AM	12/22/2020	
Gauge	7th Quad C Upper Concourse	Quarterly	10:56:53 AM	12/22/2020	
Alarm Valve	2nd Quad C Main Concourse M1-45	Quarterly	9:36:09 AM	12/22/2020	
Alarm Valve	2nd Quad C Main Concourse M-50	Quarterly	9:38:25 AM	12/22/2020	
Alarm Valve	7th Quad C Upper Concourse	Quarterly	10:56:26 AM	12/22/2020	
Control Valve	2nd Quad C Main Concourse M1-45	Quarterly	9:35:53 AM	12/22/2020	
Control Valve	2nd Quad C Main Concourse M1-45	Quarterly	9:38:11 AM	12/22/2020	
Control Valve	7th Quad C Upper Concourse M2-46	Quarterly	10:56:16 AM	12/22/2020	
Control Valve	Quad C Grounds Crew Storage Cage M1-29	Quarterly	8:44:45 AM	12/22/2020	
Control Valve	Quad C Grounds Crew Storage Cage M1-30	Quarterly	8:45:05 AM	12/22/2020	
Wet Pipe, Quad D	
Tamper Switch	Quad D Roll Up Door M1-28	Quarterly	8:24:44 AM	12/22/2020	
Tamper Switch	Quad D TSA Hall M-119	Quarterly	8:31:28 AM	12/22/2020	
Waterflow Switch	2nd Quad A Main Concourse	Quarterly	9:50:38 AM	12/22/2020	
Waterflow Switch	Quad D Roll Up Door	Quarterly	8:24:48 AM	12/22/2020	
Waterflow Switch	Quad D TSA Hall	Quarterly	8:31:33 AM	12/22/2020	
Control Valve	Quad D Roll Up Door M1-28	Quarterly	8:25:00 AM	12/22/2020	
Control Valve	Quad D TSA Hall M-119	Quarterly	8:31:24 AM	12/22/2020	
Wet Pipe, sideline	
Hose Connection	West sideline on field	Quarterly	8:49:02 AM	12/22/2020	
Wet Pipe	
Waterflow Switch	Quad D owner storage warehouse M1-19	Quarterly	11:16:25 AM	12/22/2020	
Failed/Other	
Standpipe, Quad A	
Fire Dep't Connection	Quad A FDC	Quarterly	9:07:23 AM	12/22/2020	
Standpipe, Stairway #7	
Hose Connection	1st Stairway #7	Quarterly	10:33:58 AM	12/22/2020	
Untested	
Service Main	
Fire Hydrant	Southeast				
Fire Hydrant	Northeast				
Fire Hydrant	Quad B				
Fire Hydrant	Quad A				
Fire Hydrant	Quad A				
Fire Hydrant	West Hyundai Club				
Fire Hydrant	West team store				
Fire Hydrant	Quad D				
Fire Hydrant	Quad C				
Standpipe, Quad B	
Tamper Switch	Quad B East Club/Suite Lobby Hall M1-15				
Control Valve	Quad B East Club/Suite Lobby Hall M1-15				
Standpipe, Stairway #7	
Tamper Switch	4th Stairway #7 M2-99 Atrium				
Waterflow Switch	4th Stairway #7 M2-99 Atrium				
Inspector's Test	4th Stairway #7 M2-99 Atrium				
Wet Pipe, Pirate Ship	
Special Sprinkler	Under Ship				
Sprinkler Box	Under Ship				
Sprinkler Box Spares	Under Ship				
Wrenches	Under Ship				
Wet Pipe, Quad A	
Inspector's Test	Quad A Undeveloped Space M1-19				
Wet Pipe, Quad C	
Inspector's Test	7th Quad C Upper Concourse Men’s restroom 330-331				
Wet Pipe	
Inspector's Test	Quad D owner storage warehouse M1-19				

Wet Pipe Fire Sprinkler Systems
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY		
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	unknown	unknown		6"	1	þ	57508119	
Components	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
unknown	unknown	175	36		¨	42761839	
Location	
Quad D owner storage warehouse M1-19	

Building: TAMPA SPORTS AUTHORITY	Pirate Ship	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
OS&Y	Supervisory	System Sensor	1	þ	49546384	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter	OVSR		4”	1	þ	49546382	
Components	
Alarm Valve	
Type	Manufacturer	Model #	Position	Status	Size	OK	ScanID	
Flanged by Grooved	Tyco	cv-1fp			4"	þ	49546387	
Internal Date	
12/31/1969	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Under Ship M-46	4"	Open	Supervised	þ	49546383	
Description	
Main Control	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
System Sensor	OSY2	210	NA		þ	49546385	
Location	
Under Ship	
Devices	
Drain	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	Under Ship	2"	210				þ	49546386	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	Under Ship	2"	165	165	00		þ	49546386	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	Under Ship	2"	165	165	00		þ	49546386	
Gauge	
Location	Service Date	
Under Ship	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	System Sensor	OSY2	210	NA	1/4	þ	49546392	
Gauge	
Location	Service Date	
Under Ship	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	System Sensor	OSY2	212	NA	1/4	þ	49546391	
Special Sprinkler	
Qty	Type	KFactor	Finish	Temperature	OK	ScanID	
9         	Recessed Pendant		Brass	155	¨	1	
Location	Description	Coverage	
Under Ship	Quick Response		
Sprinkler Box	
Qty	Tool Available?	SIN List?	Size	Manufacturer	Location	OK	ScanID	
7         	No		3 unit	unknown	Under Ship	¨	49546390	
Sprinkler Box Spares	
Qty	Type	Manufacturer	Location	OK	ScanID	
7         	Pendant	Tyco	Under Ship	¨	49546389	
Temperature	KFactor	Size	Finish	Response Time	
175	5.6		White	Standard Response	
Wrenches	
Qty	Type	Manufacturer	Location	OK	ScanID	
0         	Sprinkler	unknown	Under Ship	¨	49546388	

Building: TAMPA SPORTS AUTHORITY	Quad A	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546397	
Control Valve	Supervisory	Kennedy	1	þ	49546405	
Control Valve	Supervisory	Kennedy	1-2 75	þ	49546570	
Control Valve	Supervisory	Kennedy	1	þ	49546316	
Control Valve	Supervisory	Kennedy	1	þ	49546329	
Control Valve	Supervisory	Kennedy	1	þ	49546331	
Control Valve	Supervisory	Kennedy	1	þ	49546338	
Control Valve	Supervisory	Kennedy	1-76	þ	46957762	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor	WFD40		4”	1	þ	49546394	
Vane	Potter	VSR		4”	1	þ	49546566	
Vane	Potter	unknown		4”	1	þ	49546333	
Vane	Potter	unknown		4”	1	þ	49546332	
Vane	N\A	unknown		2.5”	1	þ	49546342	
Components	
Alarm Valve	
Type	Manufacturer	Model #	Position	Status	Size	OK	ScanID	
Grooved	Tyco	cv-1fr		Supervised	4"	þ	49546395	
Internal Date	
08/05/2019	
Alarm Valve	
Type	Manufacturer	Model #	Position	Status	Size	OK	ScanID	
Grooved	Tyco	cv-1fr		Supervised	4"	þ	49546406	
Internal Date	
08/05/2019	
Alarm Valve	
Type	Manufacturer	Model #	Position	Status	Size	OK	ScanID	
Grooved	Tyco	cv-1fr		Supervised	4"	þ	49546571	
Internal Date	
12/31/1969	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	2nd Quad A Main Concourse M1-51	4"	Open	Supervised	þ	49546396	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	2nd Quad A Main Concourse M1-41	4"	Open	Supervised	þ	49546404	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	7th Quad A Upper Concourse M2-75	4"	Open	Supervised	þ	49546572	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad A Catering Warehouse Restroom / Kitchen M1-	4"	Open	Supervised	þ	49546314	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad A Undeveloped Space M1-21	4"	Open	Supervised	þ	49546328	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad A Undeveloped Space M1-19	4"	Open	Supervised	þ	49546330	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad A Owners Parking M1-16	2.5"	Open	Supervised	þ	49546339	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad A Catering Warehouse M1-76	4"	Open	Supervised	þ	46957763	
Description	
Main Control	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
N\A	unknown	220	NA		þ	49546337	
Location	
Quad A Owners Parking	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
unknown	unknown	unknown	0		¨	49546334	
Location	
Quad A Undeveloped Space M1-19	
Devices	
Drain	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad A Main Concourse M1-41	2"	210		0		þ	49546398	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad A Main Concourse M1-41	2"	165	165	0		þ	49546398	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad A Main Concourse M1-41	2"	165	165	0		þ	49546398	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad A Main Concourse M1-41	2"	210		0		þ	49546407	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad A Main Concourse M1-41	2"	165	165	0		þ	49546407	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad A Main Concourse M1-41	2"	165	165	0		þ	49546407	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	7th Quad A Upper Concourse	2"	180		0		þ	49546567	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	7th Quad A Upper Concourse	2"	135	134	0		þ	49546567	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	7th Quad A Upper Concourse	2"	135	134	0		þ	49546567	
Gauge	
Location	Service Date	
2nd Quad A Main Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	unknown	210	NA	1/4	þ	49546400	
Gauge	
Location	Service Date	
2nd Quad A Main Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Wika	unknown	210	NA	1/4	þ	49546399	
Gauge	
Location	Service Date	
2nd Quad A Main Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	unknown	210	NA	1/4	þ	49546403	
Gauge	
Location	Service Date	
2nd Quad A Main Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Wika	unknown	205	NA	1/4	þ	49546402	
Gauge	
Location	Service Date	
7th Quad A Upper Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	unknown	180	NA	1/4	þ	49546569	
Gauge	
Location	Service Date	
7th Quad A Upper Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Wika	unknown	188	NA	1/4	þ	49546568	
Gauge	
Location	Service Date	
Quad A Owners Parking	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Kennedy	unknown	220	NA	1/4	þ	49546344	
Signage	
Type	Location	OK	ScanID	
Hydraulic Info	Quad A Owners Parking RJ Corridor	þ	49546341	
Hydraulic Info	Quad A Owners Parking RJ Parking	þ	49546340	

Building: TAMPA SPORTS AUTHORITY	Quad B	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546289	
Control Valve	Supervisory	Kennedy	1	þ	49546299	
Control Valve	Supervisory	Kennedy	1	þ	49546297	
Control Valve	Supervisory	Kennedy	1	þ	49546311	
Control Valve	Supervisory	Kennedy	1	þ	49546309	
Control Valve	Supervisory	Kennedy	1	þ	49546306	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter	unknown		3”	1	þ	49546305	
Vane	Potter	unknown		3”	1	þ	49546609	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad B Engineering M1-33	3"	Open	Supervised	þ	49546295	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad B Boiler M1-38	8"	Open	Supervised	þ	49546298	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	NIBCO	unknown	Quad B Boiler M1-39	8"	Open	Supervised	þ	49546296	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Quad B Food Vending M1-37	4"	Open	Supervised	þ	49546308	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad B Food Vending M1-40	4"	Open	Supervised	þ	49546310	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad B East Club/Suite Lobby Hall M1-35	2.5"	Open	Supervised	þ	49546608	
Description	
Main Control	

Building: TAMPA SPORTS AUTHORITY	Quad C	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546515	
Control Valve	Supervisory	Kennedy	1	þ	49546525	
Control Valve	Supervisory	Kennedy	1	þ	49546603	
Control Valve	Supervisory	Kennedy	1	þ	49546371	
Control Valve	Supervisory	Kennedy	1	þ	49546374	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor	WFD40		4”	1	þ	49546522	
Vane	System Sensor	WFD40		4”	1	þ	49546523	
Vane	Potter	VSR		4”	1	þ	49546599	
Vane	Kennedy	unknown		3”	1	þ	49546372	
Vane	N\A	unknown		3”	1	þ	49546375	
Components	
Alarm Valve	
Type	Manufacturer	Model #	Position	Status	Size	OK	ScanID	
Grooved	Tyco	cv-1fr		Supervised	4"	þ	57507888	
Internal Date	
12/31/1969	
Alarm Valve	
Type	Manufacturer	Model #	Position	Status	Size	OK	ScanID	
Flanged by Grooved	Tyco	cf-1fr		Supervised	4"	þ	57507889	
Internal Date	
12/31/1969	
Alarm Valve	
Type	Manufacturer	Model #	Position	Status	Size	OK	ScanID	
Grooved	Tyco	cv-1f		Supervised	4"	þ	49546604	
Internal Date	
09/19/2019	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	2nd Quad C Main Concourse M1-45	4"	Open	Supervised	þ	49546514	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	2nd Quad C Main Concourse M1-45	4"	Open	Supervised	þ	49546524	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	7th Quad C Upper Concourse M2-46	4"	Open	Supervised	þ	49546602	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad C Grounds Crew Storage Cage M1-29	3"	Open	Supervised	þ	49546370	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad C Grounds Crew Storage Cage M1-30	3"	Open	Supervised	þ	49546373	
Description	
Main Control	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
Potter	VSR	145	10		¨	49546606	
Location	
7th Quad C Upper Concourse Men’s restroom 330-331	
Devices	
Drain	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad C Main Concourse	2"	210		0		þ	49546517	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad C Main Concourse	2"	250	250	0		þ	49546517	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad C Main Concourse	2"	220	220	0		þ	49546517	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad C Main Concourse	2"	210		0		þ	49546516	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad C Main Concourse	2"	250	250	0		þ	49546516	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	2nd Quad C Main Concourse	2"	217	217	0		þ	49546516	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	7th Quad C Upper Concourse	2"	00	00	00		þ	49546605	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	7th Quad C Upper Concourse	2"	00	00	00		þ	49546605	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	7th Quad C Upper Concourse	2"	195	195	00		þ	49546605	
Gauge	
Location	Service Date	
2nd Quad C Main Concourse	09/08/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	WIKA	unknown	225	NA	1/4	þ	49546520	
Gauge	
Location	Service Date	
2nd Quad C Main Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	N\A	unknown	210	NA	1/4	þ	49546521	
Gauge	
Location	Service Date	
2nd Quad C Main Concourse	09/08/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	WIKA	unknown	210	NA	1/4	þ	49546519	
Gauge	
Location	Service Date	
2nd Quad C Main Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	WIKA	unknown	220	NA	1/4	þ	49546518	
Gauge	
Location	Service Date	
7th Quad C Upper Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	111.10sp.100	184	NA	1/4	þ	49546601	
Gauge	
Location	Service Date	
7th Quad C Upper Concourse	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Wika	49546601	185	NA	1/4	þ	49546600	

Building: TAMPA SPORTS AUTHORITY	Quad D	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546349	
Control Valve	Supervisory	Kennedy	1	þ	49546358	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	System Sensor	WFD40		4”	1	þ	49546401	
Vane	Kennedy	unknown		3”	1	þ	49546350	
Vane	N\A	unknown		3”	1	þ	49546359	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad D Roll Up Door M1-28	3"	Open	Supervised	þ	49546348	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad D TSA Hall M-119	3"	Open	Supervised	þ	49546357	
Description	
Main Control	

Building: TAMPA SPORTS AUTHORITY	field	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Devices	
Hose Connection	
Location	Size	OK	ScanID	
East sideline on field	Class I - 2.5"	þ	57507509	

Building: TAMPA SPORTS AUTHORITY	sideline	
This section lists out all the devices and components that have been associated with a Wet Pipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Hose Connection	
Location	Size	OK	ScanID	
West sideline on field	Class I - 2.5"	þ	57507508	

Standpipe Systems
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY	Quad A	
This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546327	
Control Valve	Supervisory	Kennedy	1	þ	49546320	
OS&Y	Supervisory	Kennedy	1	þ	49546323	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad A Housekeeping / Field Entry M1-9	4"	Open	Supervised	þ	49546326	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad A Housekeeping / Ramp M1-50	4"	Open	Supervised	þ	49546315	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Quad A Mechanical Room M1-22	6"	Open	Supervised	þ	49546322	
Description	
Main Control	
Devices	
Fire Dep't Connection	
Location	Type	BallDrip	Rotating Swivels	Size	OK	ScanID	
Quad A FDC	Siamese	unknown	Yes	unknown	¨	49546380	
Hose Connection	
Location	Size	OK	ScanID	
2nd Quad A Main Concourse	Class I - 2.5"	þ	49546393	
4th Quad A Club Level	Class I - 2.5"	þ	49546545	
5th Quad A Lower Suite	Class I - 2.5"	þ	49546546	
6th Quad A Upper Suite	Class I - 2.5"	þ	49546513	
7th Quad A Upper Concourse	Class I - 2.5"	þ	49546561	
Quad A Catering Warehouse	Class I - 2.5"	þ	49546313	
Quad A Ramp	Class I - 2.5"	þ	49546321	
Quad A Mechanical Room	Class I - 2.5"	þ	49546324	
Quad A Players Corridor	Class I - 2.5"	þ	49546335	
Quad A Field Entry	Class I - 2.5"	þ	57508118	

Building: TAMPA SPORTS AUTHORITY	Quad B	
This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546301	
Control Valve	Supervisory	Potter	1	þ	49546317	
Control Valve	Supervisory	Kennedy	1	¨	49546304	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad B Delivery Swing Gate M1-49	4"	Open	Supervised	þ	49546300	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Quad B Chiller M1-47	8"	Open	Supervised	þ	49546319	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	N\A	unknown	Quad B East Club/Suite Lobby Hall M1-15	2.5"			¨	49546303	
Description	
Main Control	
Devices	
Fire Dep't Connection	
Location	Type	BallDrip	Rotating Swivels	Size	OK	ScanID	
Quad B FDC	Siamese	unknown	Yes	unknown	þ	49546261	
Hose Connection	
Location	Size	OK	ScanID	
2nd Quad B Main Concourse	Class I - 2.5"	þ	49546527	
4th Quad B / C Club Level	Class I - 2.5"	þ	49546573	
4th Quad B Club Level	Class I - 2.5"	þ	49546598	
5th Quad B / C Lower Suite	Class I - 2.5"	þ	49546581	
5th Quad B Lower Suite	Class I - 2.5"	þ	49546580	
6th Quad B / C Ford Super Suite	Class I - 2.5"	þ	49546588	
6th Quad B Ford Super Suite Pantry / Stairway 2	Class I - 2.5"	þ	49546594	
7th Quad B Upper Concourse	Class I - 2.5"	þ	49546595	
Quad B Delivery Swing Gate	Class I - 2.5"	þ	49546302	
Quad B Field Entry	Class I - 2.5"	þ	49546312	
Quad B East Club/Suite Lobby Hall	Class I - 2.5"	þ	49546307	
Quad B Chiller	Class I - 2.5"	þ	49546318	

Building: TAMPA SPORTS AUTHORITY	Quad C	
This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546365	
Control Valve	Supervisory	Kennedy	1	þ	49546378	
OS&Y	Supervisory	Kennedy	1	þ	49546368	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad C Tunnel / Grounds Crew M1-26	4"	Open	Supervised	þ	49546364	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad C Middle Hall M1-24	2.5"	Open	Supervised	þ	49546377	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Quad C Mechanical M1-34	6"	Open	Supervised	þ	49546367	
Description	
Main Control	
Devices	
Fire Dep't Connection	
Location	Type	BallDrip	Rotating Swivels	Size	OK	ScanID	
Quad C FDC	Siamese	unknown	Yes	unknown	þ	49546381	
Hose Connection	
Location	Size	OK	ScanID	
2nd Quad C Main Concourse	Class I - 2.5"	þ	49546526	
4th Quad C Club Level	Class I - 2.5"	þ	49546579	
5th Quad C Lower Suite	Class I - 2.5"	þ	49546587	
6th Quad C Upper Suite	Class I - 2.5"	þ	49546593	
7th Quad C Upper Concourse	Class I - 2.5"	þ	49546607	
Quad C Tunnel / Grounds Crew	Class I - 2.5"	þ	57507887	
Quad C Mechanical	Class I - 2.5"	þ	49546369	
Quad C Field Entry	Class I - 2.5"	þ	49546363	
Quad C Middle Hall	Class I - 2.5"	þ	49546376	

Building: TAMPA SPORTS AUTHORITY	Quad D	
This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546346	
Control Valve	Supervisory	Kennedy	1	þ	49546353	
OS&Y	Supervisory	Kennedy	1	þ	49546355	
Control Valve	Supervisory	Kennedy	1	þ	49546362	
Control Valve	Supervisory	Kennedy	1-1 104	þ	57508120	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Quad D Players Entrance M1-25	2"	Open	Supervised	þ	49546345	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad D Roll Up Door M1-27	4"	Open	Supervised	þ	49546351	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Quad D Mechanical M1-30	6"	Open	Supervised	þ	49546354	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad D TSA Hall M1-29	4"	Open	Supervised	þ	49546361	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Quad D Buccs Warehouse HR Door 2 locker	6"	Open	Supervised	þ	57508121	
Description	
Isolation	
Devices	
Fire Dep't Connection	
Location	Type	BallDrip	Rotating Swivels	Size	OK	ScanID	
Quad D FDC	Siamese	unknown	Yes	unknown	þ	49546379	
Hose Connection	
Location	Size	OK	ScanID	
2nd Quad D Main Concourse	Class I - 2.5"	þ	49546413	
4th Quad A / D Club Level	Class I - 2.5"	þ	49546544	
4th Quad D Club Level	Class I - 2.5"	þ	49546543	
5th Quad A / D Lower Suite	Class I - 2.5"	þ	49546552	
5th Quad D Lower Suite	Class I - 2.5"	þ	49546553	
6th Quad D	Class I - 2.5"	þ	49546565	
6th Quad A / D Press Box	Class I - 2.5"	þ	49546559	
6th Quad D Press Box	Class I - 2.5"	þ	49546560	
Quad D Players Corridor	Class I - 2.5"	þ	49546336	
Quad D Roll Up Door	Class I - 2.5"	þ	49546352	
Quad D TSA Hall	Class I - 2.5"	þ	49546360	
Quad D Field Entry	Class I - 2.5"	þ	49546347	
Quad D Mechanical	Class I - 2.5"	þ	49546356	

Building: TAMPA SPORTS AUTHORITY	Stairway #6	
This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546530	
Control Valve	Supervisory	Kennedy	1	þ	49546533	
Control Valve	Supervisory	Kennedy	1	þ	49546576	
Control Valve	Supervisory	Kennedy	1	þ	49546583	
Control Valve	Supervisory	Kennedy	1	þ	49546589	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter	VSR		4"	1	þ	49546577	
Vane	Potter	VSR		4”	1	þ	49546585	
Vane	Potter	VSR		4"	1	þ	49546592	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	2nd Stairway #6 M2-15	8"	Open	Supervised	þ	49546529	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	3rd Stairway #6 M2-14	4"	Open	Supervised	þ	49546532	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	4th Stairway #7 M2-13 Club Level	4"	Open	Supervised	þ	49546575	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	5th Stairway #6 M2-24 Lower Suite	4"	Open	Supervised	þ	49546582	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	6th Stairway #6 M2-35 Upper Suite	4"	Open	Supervised	þ	49546590	
Description	
Main Control	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
unknown	unknown		83		þ	49546574	
Location	
4th Stairway #6 Club Level	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
unknown	unknown		NA		þ	49546584	
Location	
5th Stairway #6 Lower Suite	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
AGF	unknown		NA		þ	49546591	
Location	
6th Stairway #6 Upper Suite	
Devices	
Gauge	
Location	Service Date	
7th Stairway #6	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	WIKA	111.10sp.100	185	NA	1/4	þ	49546597	
Hose Connection	
Location	Size	OK	ScanID	
1st Stairway #6	Class I - 2.5"	þ	49546528	
3rd Stairway #6	Class I - 2.5"	þ	49546531	
4th Stairway #6	Class I - 2.5"	þ	49546578	
5th Stairway #6	Class I - 2.5"	þ	49546586	
7th Stairway #6	Class I - 2.5"	þ	49546596	

Building: TAMPA SPORTS AUTHORITY	Stairway #7	
This section lists out all the devices and components that have been associated with a Standpipe System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	Kennedy	1	þ	49546409	
Control Valve	Supervisory	Kennedy	1	þ	49546412	
Control Valve	Supervisory	Kennedy	1	þ	49546535	
Control Valve	Supervisory	Kennedy	1	þ	49546548	
Control Valve	Supervisory	Kennedy	1	þ	49546555	
Control Valve	Supervisory	Kennedy	1	¨	49546541	
Waterflow Switch	
Type	Manufacturer	Model #	Sec	Size	Zone/Address	OK	ScanID	
Vane	Potter	VSR		4"	1	þ	49546537	
Vane	Potter	VSR		4”	1	þ	49546549	
Vane	Potter	VSR		4"	1	þ	49546557	
Vane	unknown	unknown		4"	1	¨	57508117	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	2nd Stairway #7 M2-5	8"	Open	Supervised	þ	49546408	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	3rd Stairway #7 M2-29	4"	Open	Supervised	þ	49546411	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	4th Stairway #7 M2-7 Club Level	4"	Open	Supervised	þ	49546534	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	4th Stairway #7 M2-99 Atrium	4"	Open	Supervised	þ	49546540	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	5th Stairway #7 M2-7 Lower Suite	4"	Open	Supervised	þ	49546547	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	6th Stairway #7 M2-57 Upper Suite	4"	Open	Supervised	þ	49546554	
Description	
Main Control	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
unknown	unknown	200	NA		þ	49546536	
Location	
4th Stairway #7 Club Level	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
unknown	unknown		NA		þ	49546550	
Location	
5th Stairway #7 Lower Suite	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
AGF	M1000		NA		þ	49546556	
Location	
6th Stairway #7 Upper Suite	
Inspector's Test	
Manufacturer	Model #	Pressure psi	Valve Trip Time sec	Water Flow Time sec	OK	ScanID	
unknown	unknown	150	41		¨	49546538	
Location	
4th Stairway #7 M2-99 Atrium	
Devices	
Gauge	
Location	Service Date	
4th Stairway #7 M2-99 Atrium	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	unknown	unknown	200	NA	1/4	þ	57508116	
Gauge	
Location	Service Date	
7th Stairway #7	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	unknown	unknown	185	NA	1/4	þ	49546564	
Hose Connection	
Location	Size	OK	ScanID	
5th Stairway #7	Class I - 2.5"	þ	49546551	
6th Stairway #7	Class I - 2.5"	þ	49546558	
7th Stairway #7	Class I - 2.5"	þ	49546562	
7th Stairway #7	Class I - 2.5"	þ	49546563	
1st Stairway #7	Class I - 2.5"	¨	49546410	

Private Fire Service Mains
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY		
This section lists out all the devices and components that have been associated with a Private Fire Service Main and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Devices	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
Southeast	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508122	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1060	44	40	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
Northeast	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508123	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1130	56	46	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
Quad B	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508124	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1130	54	44	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
Quad A	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508125	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1000	54	40	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
Quad A	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508126	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1060	54	40	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
West Hyundai Club	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508127	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1060	50	41	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
West team store	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508128	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1000	58	41	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
Quad D	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508129	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1060	59	40	Closed against pressure	09/08/2020	
Fire Hydrant	
Location	Mfr	Model	Type	Position	Size	OK	ScanID	
Quad C	Clow	AWWA	Dry Barrel/Ground		5.25”	¨	57508130	
Description	Orifice	Flow Rate	Static	Residual	Valve Type	Flush Test Date	
1000 gpm/3786 lpm	2@2-1/2" and 1@4 1/2"	1060	52	40	Closed against pressure	09/08/2020	

Preaction Fire Sprinkler Systems
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY	Control Room	
This section lists out all the devices and components that have been associated with a Preaction System and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Air Compressor	
Location	Mfr.	Model #	Phase	On psi	Off psi	Serial No.	
Control Room Low Air	Gast	unknown	1	unknown	12	N\A	
Type	Description	Rated Speed	Horsepower	Volts	Amps	OK	ScanID	
Automatic	Tank	1725	1/6	115	3.5	þ	49546426	
Air Maintenance Device	
Type	Model #	Location	Install Date	Air Pressure	ScanID	
Pressure Reducing	unknown	Control Room	01/01/1998	10	49546423	
Alarms	
Pressure Switch	
Type	Description	Manufacturer	Low	High	Zone/Address	OK	ScanID	
Pressure Switch	Alarm	System Sensor	n/a	n/a	1	þ	49546422	
Pressure Switch	Supervisory	System Sensor	n/a	n/a	1	þ	49546421	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
Control Valve	Supervisory	System Sensor	1	þ	49546420	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	System Sensor	EPS10-2	Upper Suite A Control Room Main Control	2.5"	Open	Supervised	þ	49546419	
Description	
Main Control	
Preaction Valve	
Manufacturer	Model #	Serial #	Size	OK	ScanID	
Reliable	DDX	unknown	2.5"	þ	49546262	
Type	Position	Status	Location	Solenoid	Timing (sec)	
Double Interlock		Supervised	Control Room	24vdc		
Water psi	Air Pressure	Trip Air psi	Trip Time	
190	10	n/a	n/a	
Devices	
Drain	
Current Inspection	
Type	Location	Size	Supply psi	Restored psi	Residual psi	Sec	OK	ScanID	
Main	Control Room	1.25"	190		n/a		þ	49546425	
Previous Inspections	
September 8, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	Control Room	1.25"	175	175	n/a		þ	49546425	
June 2, 2020	
Type	Location	Size	Supply psi	Static psi	Residual psi	Sec	OK	ScanID	
Main	Control Room	1.25"	175	175	n/a		þ	49546425	
Gauge	
Location	Service Date	
Control Room	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Air Pressure	Wika	unknown	10	n/a	1/4	þ	49546427	
Gauge	
Location	Service Date	
Control Room	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Wika	unknown	190	n/a	1/4	þ	49546415	
Gauge	
Location	Service Date	
Control Room	09/08/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
System Pressure	Wika	unknown	190	n/a	1/4	þ	49546416	
Gauge	
Location	Service Date	
Control Room	09/08/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Air Pressure	Wika	unknown	8	n/a	1/4	þ	49546417	
Gauge	
Location	Service Date	
Control Room	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Air Pressure	Wika	unknown	10	n/a	1/4	þ	49546418	
Gauge	
Location	Service Date	
Control Room	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Air Pressure	Wika	unknown	10	n/a	1/4	þ	49546424	

Fire Pump Testing
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY		
This section lists out all the devices and components that have been associated with a Fire Pump and provides details as to type of component, pressure readings, response time, etc. If a component has an OK checkbox that is checked, then that component was actually tested. However, for Pass/Fail test results, see the Inspection and Testing section.	

Controller	
Manufacturer	Model #	Location	Install Date	Serial Number	
Master	mcttz225-125-46-fx	Pump Room	01/22/2015	78756	
AC Power	Time Meter	Start psi	Stop psi	Battery Supervised	Generator Backup	
		155		No	Yes	
Electrical	
Manufacturer	Model #	Location	Serial Number	ScanID	
U.S. Electrical Moto	H632	Fire Pump Room	H632-A11A260R150M	57507886	
Timing Min/Sec		
Full	Run	Volts	Amps	Horsepower	Rated Speed	
		460	137	125	3565	
Fire Pump Gauge	
Location	Discharge psi	Suction psi	OK	ScanID	
Jockey Pump Discharge		50	þ	49546266	
Jockey Pump Discharge	56		þ	49546277	
Controller	
Manufacturer	Model #	Location	Install Date	Serial Number	
Master	pic-3-3-46-12	Jockey Pump Controller	01/22/2015	78756	
AC Power	Time Meter	Start psi	Stop psi	Battery Supervised	Generator Backup	
		150	170	No	No	
Jockey Pump	
Manufacturer	Model Number	Location	Install Date	Scan Number	
Baldor	84.z00011	Fire Pump Room	01/22/2015	57507884	
Serial Number	Type	Horse Pwr	Rated Spd	Volts	Amps	On psi	Off psi	
n/a	Automatic	3	3540	208-230/460	8.4-8/4	150	170	
Pump	
Manufacturer	Model Number	Location	Install Date	Scan Number	
Patterson	6x5 MAAH	Fire Pump Room	01/01/1998	57507885	
Serial Number	Type	Orientation	Aligned?	Water Supply	Impeller Size	
FP-c12613	Pump Primary	Horizontal	Yes	Municipal	9.50	
Alarms	
Tamper Switch	
Type	Description	Manufacturer	Zone/Address	OK	ScanID	
OS&Y	Supervisory	Potter	1	þ	49546264	
OS&Y	Supervisory	Potter	1	þ	49546275	
Control Valve	Supervisory	Kennedy	1	þ	49546282	
Control Valve	Supervisory	Kennedy	1	þ	49546287	
Control Valve	Supervisory	Kennedy	1	þ	49546343	
Components	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Fire Pump Suction	8"	Open	Supervised	þ	49546263	
Description	
Suction	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Kennedy	unknown	Fire Pump Test Header	8"	Closed	Supervised	þ	49546274	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	United	unknown	Jockey Pump Discharge	1.25"	Open		þ	49546280	
Description	
Main Control	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Fire Pump Discharge	8"	Open	Supervised	þ	49546281	
Description	
Discharge	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
OS&Y	Wika	unknown	Jockey Pump Suction	1.25"	Open		þ	49546268	
Description	
Isolation	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Fire Pump Bypass	8"	Open	Supervised	þ	49546285	
Description	
Bypass	
Control Valve	
Type	Manufacturer	Model	Location	Size	Position	Status	OK	ScanID	
Butterfly	Kennedy	unknown	Fire Pump Bypass	8"	Open	Supervised	þ	49546284	
Description	
Bypass	
Devices	
Gauge	
Location	Service Date	
Fire Pump Controller	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	unknown	222	NA	1/4	þ	49546267	
Gauge	
Location	Service Date	
Fire Pump Relief Valve	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	111.10sp.100	50	NA	1/4	þ	49546288	
Gauge	
Location	Service Date	
Fire Pump Relief Valve	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	111.10sp.100	222	NA	1/4	þ	49546276	
Gauge	
Location	Service Date	
Jockey Pump Discharge	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	111.10sp.100	60	NA	1/4	þ	49546290	
Gauge	
Location	Service Date	
Jockey Pump Controller	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	111.10sp.100	222	NA	1/4	þ	49546278	
Gauge	
Location	Service Date	
Jockey Pump Suction	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	unknown	60	NA	1/4	þ	49546283	
Gauge	
Location	Service Date	
Jockey Pump Controller	12/22/2020	
Type	Manufacturer	Model #	Static psi	Fill Type	Size	OK	ScanID	
Supply Pressure	Wika	unknown	225	NA	1/4	þ	49546273	
Signage	
Type	Location	OK	ScanID	
Hydraulic Info	Control Room	þ	49546271	
Hydraulic Info	Home Team Locker Room	þ	49546270	
Hydraulic Info	Team Store Atrium	þ	49546269	

Signage Report
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY	
This section documents a list of signage applicable to the system(s) in this building.	

Signage	
Type	Location	OK	ScanID	
Hydraulic Info	Control Room	þ	49546271	
Hydraulic Info	Home Team Locker Room	þ	49546270	
Hydraulic Info	Team Store Atrium	þ	49546269	
Hydraulic Info	Quad A Owners Parking RJ Corridor	þ	49546341	
Hydraulic Info	Quad A Owners Parking RJ Parking	þ	49546340	

Inventory & Warranty Report	
Generated by: BuildingReports.com	
Building: TAMPA SPORTS AUTHORITY	
The Inventory & Warranty Report lists each of the devices and items that are included in your Inspection Report. A complete inventory count by device type and category is provided. Items installed within the last 90 days, within the last year, and devices installed for two years or more are grouped together for easy reference.	

Device or Type	Category	% of Inventory	Quantity	
Special Sprinkler	Sprinkler	0.36%	1	
Inspector's Test	Valve	4.27%	12	
Control Valve	Valve	19.57%	55	
Tamper Switch	Alarm	18.86%	53	
Wrenches	Sprinkler	0.36%	1	
Sprinkler Box Spares	Sprinkler	0.36%	1	
Sprinkler Box	Sprinkler	0.36%	1	
Fire Hydrant	Hose	3.20%	9	
Waterflow Switch	Alarm	8.54%	24	
Fire Dep't Connection	Hose	1.42%	4	
Gauge	Device	11.03%	31	
Controller	Pump	0.36%	1	
Electrical Driver	Pump	0.36%	1	
Fire Pump Gauge	Pump	0.71%	2	
Jockey Pump	Pump	0.36%	1	
Jockey Controller	Pump	0.36%	1	
Hose Connection	Hose	19.93%	56	
Signage	Sprinkler	1.78%	5	
Alarm Valve	Valve	2.49%	7	
Drain	Device	2.85%	8	
Control Panel	Alarm	0.36%	1	
Preaction Valve	Valve	0.36%	1	
Pressure Switch	Alarm	0.71%	2	
Air Maintenance Device	Pump	0.36%	1	
Air Compressor	Pump	0.36%	1	
Pump	Pump	0.36%	1	

Device Type	Qty	Model #	Type	Description	Install Date	
In Service - 90 Days - 1 Year	
Fire Pump	
Fire Pump Gauge	1	unknown	Suction		03/04/2020	
Fire Pump Gauge	1	111.10sp.100	Discharge		03/04/2020	
Gauge	4	111.10sp.100	Supply Pressure		03/04/2020	
Gauge	2	unknown	Supply Pressure		03/04/2020	
Preaction, Control Room	
Gauge	4	unknown	Air Pressure		03/04/2020	
Gauge	2	unknown	System Pressure		03/04/2020	
Standpipe, Stairway #7	
Gauge	1	unknown	System Pressure		03/04/2020	
Wet Pipe, Pirate Ship	
Gauge	1	OSY2	Supply Pressure		03/04/2020	
Gauge	1	OSY2	System Pressure		03/04/2020	
Wet Pipe, Quad A	
Gauge	1	unknown	System Pressure		03/04/2020	
Gauge	3	unknown	Supply Pressure		03/04/2020	
Gauge	3	unknown	System Pressure		03/04/2020	
Wet Pipe, Quad C	
Gauge	1	unknown	Supply Pressure		03/04/2020	
Gauge	1	111.10sp.100	Supply Pressure		03/04/2020	
Gauge	1	49546601	System Pressure		03/04/2020	
Gauge	1	unknown	Supply Pressure		03/04/2020	
Gauge	2	unknown	System Pressure		03/04/2020	
In Service - 5 Years to 10 Years	
Fire Pump	
Jockey Pump	1	84.z00011	Automatic		01/22/2015	
Controller	1	mcttz225-125-46-fx		Automatic	01/22/2015	
Jockey Controller	1	pic-3-3-46-12			01/22/2015	
Signage	3	unknown	Hydraulic Info		01/22/2015	
Control Valve	1	unknown	OS&Y	Isolation	01/22/2015	
Gauge	1	unknown	Supply Pressure		01/22/2015	
Standpipe, Stairway #6	
Gauge	1	111.10sp.100	System Pressure		01/22/2015	
Wet Pipe, Quad A	
Signage	1	unknown	Hydraulic Info		01/22/2015	
Signage	1	unknown	Hydraulic Info		01/22/2015	
Alarm Valve	2	cv-1fr	Grooved		01/22/2015	
Wet Pipe, Quad C	
Alarm Valve	1	cv-1f	Grooved		01/22/2015	
In Service - 15 Years to 25 Years	
Fire Pump	
Control Valve	2	unknown	Butterfly	Bypass	01/01/1998	
Control Valve	1	unknown	Butterfly	Discharge	01/01/1998	
Control Valve	1	unknown	OS&Y	Main Control	01/01/1998	
Control Valve	1	unknown	OS&Y	Suction	01/01/1998	
Tamper Switch	3	unknown	Control Valve	Supervisory	01/01/1998	
Pump	1	6x5 MAAH	Pump Primary		01/01/1998	
Tamper Switch	2	OSYSU-2	OS&Y	Supervisory	01/01/1998	
Electrical Driver	1	H632			01/01/1998	
Control Valve	1	unknown	OS&Y	Main Control	01/01/1998	
Preaction, Control Room	
Air Compressor	1	unknown	Automatic	Tank	01/01/1998	
Control Panel	1	PFC-4410RC			01/01/1998	
Preaction Valve	1	DDX	Double Interlock		01/01/1998	
Control Valve	1	EPS10-2	Butterfly	Main Control	01/01/1998	
Pressure Switch	1	EPS10-2	Pressure Switch	Alarm	01/01/1998	
Pressure Switch	1	EPS10-2	Pressure Switch	Supervisory	01/01/1998	
Tamper Switch	1	EPS10-2	Control Valve	Supervisory	01/01/1998	
Air Maintenance Device	1	unknown	Pressure Reducing		01/01/1998	
Drain	1	unknown	Main		01/01/1998	
Service Main	
Fire Hydrant	9	AWWA	Dry Barrel/Ground	1000 gpm/3786 lpm	01/01/1998	
Standpipe, Quad A	
Control Valve	2	unknown	Butterfly	Main Control	01/01/1998	
Control Valve	1	unknown	OS&Y	Main Control	01/01/1998	
Tamper Switch	2	unknown	Control Valve	Supervisory	01/01/1998	
Tamper Switch	1	unknown	OS&Y	Supervisory	01/01/1998	
Fire Dep't Connection	1	unknown	Siamese		01/01/1998	
Hose Connection	10	unknown			01/01/1998	
Standpipe, Quad B	
Control Valve	1	unknown	Butterfly	Main Control	01/01/1998	
Control Valve	1	unknown	OS&Y	Main Control	01/01/1998	
Tamper Switch	2	unknown	Control Valve	Supervisory	01/01/1998	
Control Valve	1	unknown	Butterfly	Main Control	01/01/1998	
Hose Connection	1	unknown			01/01/1998	
Tamper Switch	1	unknown	Control Valve	Supervisory	01/01/1998	
Fire Dep't Connection	1	unknown	Siamese		01/01/1998	
Hose Connection	11	unknown			01/01/1998	
Standpipe, Quad C	
Control Valve	2	unknown	Butterfly	Main Control	01/01/1998	
Control Valve	1	unknown	OS&Y	Main Control	01/01/1998	
Hose Connection	2	unknown			01/01/1998	
Tamper Switch	2	unknown	Control Valve	Supervisory	01/01/1998	
Tamper Switch	1	unknown	OS&Y	Supervisory	01/01/1998	
Fire Dep't Connection	1	unknown	Siamese		01/01/1998	
Hose Connection	7	unknown			01/01/1998	
Standpipe, Quad D	
Control Valve	1	unknown	Butterfly	Isolation	01/01/1998	
Control Valve	2	unknown	Butterfly	Main Control	01/01/1998	
Control Valve	2	unknown	OS&Y	Main Control	01/01/1998	
Tamper Switch	4	unknown	Control Valve	Supervisory	01/01/1998	
Tamper Switch	1	unknown	OS&Y	Supervisory	01/01/1998	
Fire Dep't Connection	1	unknown	Siamese		01/01/1998	
Hose Connection	13	unknown			01/01/1998	
Standpipe, Stairway #6	
Inspector's Test	1	unknown			01/01/1998	
Control Valve	4	unknown	Butterfly	Main Control	01/01/1998	
Control Valve	1	unknown	OS&Y	Main Control	01/01/1998	
Tamper Switch	5	unknown	Control Valve	Supervisory	01/01/1998	
Hose Connection	1	unknown			01/01/1998	
Waterflow Switch	3	VSR	Vane	Alarm	01/01/1998	
Hose Connection	4	unknown			01/01/1998	
Inspector's Test	2	unknown			01/01/1998	
Standpipe, Stairway #7	
Inspector's Test	1	M1000			01/01/1998	
Control Valve	6	unknown	Butterfly	Main Control	01/01/1998	
Tamper Switch	6	unknown	Control Valve	Supervisory	01/01/1998	
Waterflow Switch	3	VSR	Vane	Alarm	01/01/1998	
Gauge	1	unknown	System Pressure		01/01/1998	
Hose Connection	5	unknown			01/01/1998	
Inspector's Test	3	unknown			01/01/1998	
Waterflow Switch	1	unknown	Vane	Alarm	01/01/1998	
Wet Pipe	
Inspector's Test	1	unknown			01/01/1998	
Waterflow Switch	1	unknown	Vane	Alarm	01/01/1998	
Wet Pipe, field	
Hose Connection	1	unknown			01/01/1998	
Wet Pipe, Pirate Ship	
Control Valve	1	unknown	Butterfly	Main Control	01/01/1998	
Waterflow Switch	1	OVSR	Vane	Alarm	01/01/1998	
Drain	1	OSY2	Main		01/01/1998	
Inspector's Test	1	OSY2			01/01/1998	
Tamper Switch	1	OSY2	OS&Y	Supervisory	01/01/1998	
Alarm Valve	1	cv-1fp	Flanged by Grooved		01/01/1998	
Special Sprinkler	1	329	Recessed Pendant	Quick Response	01/01/1998	
Sprinkler Box Spares	1	329	Pendant		01/01/1998	
Sprinkler Box	1	unknown			01/01/1998	
Wrenches	1	unknown	Sprinkler		01/01/1998	
Wet Pipe, Quad A	
Control Valve	8	unknown	Butterfly	Main Control	01/01/1998	
Drain	2	unknown	Main		01/01/1998	
Tamper Switch	8	unknown	Control Valve	Supervisory	01/01/1998	
Inspector's Test	1	unknown			01/01/1998	
Waterflow Switch	1	unknown	Vane	Alarm	01/01/1998	
Waterflow Switch	2	unknown	Vane	Alarm	01/01/1998	
Waterflow Switch	1	VSR	Vane	Alarm	01/01/1998	
Waterflow Switch	1	WFD40	Vane	Alarm	01/01/1998	
Alarm Valve	1	cv-1fr	Grooved		01/01/1998	
Drain	1	unknown	Main		01/01/1998	
Inspector's Test	1	unknown			01/01/1998	
Wet Pipe, Quad B	
Control Valve	4	unknown	Butterfly	Main Control	01/01/1998	
Control Valve	1	unknown	OS&Y	Main Control	01/01/1998	
Tamper Switch	6	unknown	Control Valve	Supervisory	01/01/1998	
Control Valve	1	unknown	Butterfly	Main Control	01/01/1998	
Waterflow Switch	2	unknown	Vane	Alarm	01/01/1998	
Wet Pipe, Quad C	
Control Valve	5	unknown	Butterfly	Main Control	01/01/1998	
Tamper Switch	5	unknown	Control Valve	Supervisory	01/01/1998	
Waterflow Switch	1	unknown	Vane	Alarm	01/01/1998	
Waterflow Switch	1	unknown	Vane	Alarm	01/01/1998	
Inspector's Test	1	VSR			01/01/1998	
Waterflow Switch	1	VSR	Vane	Alarm	01/01/1998	
Waterflow Switch	2	WFD40	Vane	Alarm	01/01/1998	
Alarm Valve	1	cf-1fr	Flanged by Grooved		01/01/1998	
Alarm Valve	1	cv-1fr	Grooved		01/01/1998	
Drain	3	unknown	Main		01/01/1998	
Wet Pipe, Quad D	
Control Valve	2	unknown	Butterfly	Main Control	01/01/1998	
Tamper Switch	2	unknown	Control Valve	Supervisory	01/01/1998	
Waterflow Switch	1	unknown	Vane	Alarm	01/01/1998	
Waterflow Switch	1	unknown	Vane	Alarm	01/01/1998	
Waterflow Switch	1	WFD40	Vane	Alarm	01/01/1998	
Wet Pipe, sideline	
Hose Connection	1	unknown			01/01/1998	

Zone Address Report
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY	
The Zone Address Report lists all of the devices and items that have an individual address, or are grouped together under a common zone.  The device type, location and description are included for your reference. For more information on the device, use the link provided under ScanID.	
Address	Device Type	Location	Type	ScanID	
Control Panel 1	
Zone/Address: 1	
104	Control Valve	Quad D Buccs Warehouse HR Door 2 locker	Butterfly	57508121	
104	Tamper Switch	Quad D Buccs Warehouse HR Door 2 locker	Control Valve	57508120	
Zone/Address: 2	
75	Control Valve	7th Quad A Upper Concourse M2-75	Butterfly	49546572	
75	Tamper Switch	7th Quad A Upper Concourse M2-75	Control Valve	49546570	
Zone/Address: 3	
33	Control Valve	Upper Suite A Control Room Main Control	Butterfly	49546419	
76	Control Valve	Quad A Catering Warehouse M1-76	Butterfly	46957763	
76	Tamper Switch	Quad A Catering Warehouse M1-76	Control Valve	46957762	

Notes & Recommendations
Generated by: BuildingReports.com

Building: TAMPA SPORTS AUTHORITY	
The Notes & Recommendations Report details additional inspection notes made by the Inspectors during the course of the building inspection. Notes are grouped by SystemID.	
General Note	
No Access to untested devices or not part of quarterly inspection.	
Note	Device Type	Location	Comment	ScanID	
Service Main	
2	Fire Hydrant	Quad A		57508125	
Missing blue road reflector and 2.5” cap	
3	Fire Hydrant	West Hyundai Club		57508127	
Missing Road marker
Improper clearance around hydrant and to the ground needs 18” on both	
Standpipe, Quad D	
4	Control Valve	Quad D Roll Up Door M1-27	Passed	49546351	
Could not test due to missing chains see tamper device for M1- 27 for photos	
Wet Pipe, Quad A	
5	Tamper Switch	Quad A Catering Warehouse Restroom / Kitchen M1-	Passed	49546316	
No tamper